## Doc & Version Control
Document Control
Field | Value
Project | Green Valley Conceptual Mining Site Office & Workshop Electrical Distribution Design
Document | Load & Maximum Demand and Input Analysis
Status | Preliminary
Revision | Rev 01
Prepared by | Eason Zhu
Date | 2026-09-17
Design Case | Rev 01 Maximum Demand
Version Control
Revision | Description of Changes | Date
Rev 00 | Initial preliminary issue | —
Rev 01 | Updated load inputs, feeder allocation and maximum demand results; updated preliminary transformer sizing basis. | 2026-09-17

## Summary
Design Summary | Result
Revision | Rev 01
Calculated Maximum Demand | 62.068 kVA
Project Spare Capacity | 25%
Design Demand | 77.585 kVA
Preliminary Transformer | 100 kVA, 11/0.415 kV
Transformer loading at calculated MD | 62.01%
Transformer loading incl. design reserve | 77.58%
Next verification | Load Flow + voltage drop + motor starting
Load Flow Input Summary
Office Feeder | P=16.743 kW, Q=5.555 kVAr, S=17.641 kVA, PF=0.949 lagging
Workshoop Feeder | P=36.684 kW, Q=26.036 kVAr, S=44.984 kVA, PF=0.815 lagging
Total: | P=53.427 kW, Q=31.591 kVAr, S=62.068 kVA, PF=0.861 lagging

## Load & Max Demand Analysis
Area | Load ID | Equipment / Service | Qty | Supply | Unit Rating | Operating Basis | Maximum Demand Basis / Classification | Maximum Demand Treatment / Contribution | Design Basis / Notes | Reference ID
Office | LD-OF-01 | Double GPO provision | 15 double = 30 outlets | 230 V 1φ | / | / | AS/NZS 3000 non-domestic socket-outlet calculation Load Group (b) (ii) | 3.900 kW | 72 m² ÷ 5 m² per double GPO → 15 double GPOs. Curtin guideline specifies one double GPO per 5 m² for typical office space. | REF-OF-01
Office | LD-OF-02 | Laptop + monitor workstation | 8 | 230 V 1φ | 65 W laptop adapter + 65 W max monitor | Continuous during office hours | AS/NZS 3000 non-domestic socket-outlet calculation Load Group (b) (ii) | Calculated at Table C2 group (b)(ii) (GPO Group) | 8 staff from 72 m² office. Dell 65 W USB-C adapter and P2425H monitor max 65 W. | REF-OF-02
Office | LD-OF-03 | Shared multifunction printer | 1 | 230 V 1φ | 920 W peak | Intermittent | AS/NZS 3000 non-domestic socket-outlet calculation Load Group (b) (ii) | Calculated at Table C2 group (b)(ii) (GPO Group) | Brother MFC-L2880DW, manufacturer specifies average peak 920 W. | REF-OF-03
Office | LD-OF-04 | Paper shredder | 1 | 230 V 1φ | 460 W motor | Intermittent | AS/NZS 3000 non-domestic socket-outlet calculation Load Group (b) (ii) | Calculated at Table C2 group (b)(ii) (GPO Group) | Fellowes 99Ci is a small-office shredder, Australian supplier data gives 460 W motor, 230 V/50 Hz. | REF-OF-04
Office | LD-OF-05 | Standing fan | 1 | 230 V 1φ | 35 W | Intermittent / user-controlled | AS/NZS 3000 non-domestic socket-outlet calculation Load Group (b) (ii) | Calculated at Table C2 group (b)(ii) (GPO Group) | Dimplex DCACP30DC pedestal air-circulator fan, manufacturer rated power 35 W. | REF-OF-05
Office | LD-OF-06 | Toilet / washroom exhaust fan | 1 | 230 V 1φ | 20 W | Cycling / occupancy controlled | 100% conservative, included in lighting group (a) | 0.020 kW | Fantech SILDES300CZ3C-S, input 0.02 kW. | REF-OF-06
Office | LD-OF-07 | Split-system HVAC | 2 | 230 V 1φ | 3.65 kW max electrical input each 7.1 kW cooling | Cycling / automatic | heating/cooling/appliance group calculation AS/NZS 3000, table C2, Group (c) , colomn 3 | Calculated at Table C2 group (c) | Two preliminary HVAC zones. MHI Bronte 7.1 kW model: 1.84 kW nominal cooling input, 3.65 kW maximum input. Final selection requires mechanical heat-load calculation. | REF-OF-07
Office | LD-OF-08 | LED panel lighting | 8 | 230 V 1φ | 36 W/fitting | Continuous when occupied | 100% connected lighting load AS/NZS 3000, table C2, Group (a), colomn 3 | 0.288 kW | Preliminary 4×2 layout in 72 m² office, Pierlite ECO Panel Gen3, final quantity subject to photometric calculation. | REF-OF-08
Office (Communication) | LD-OF-09 | 16-port PoE network switch | 1 | 230 V 1φ | 141.4 W worst-case incl. PoE | Continuous | AS/NZS 3000 Cl.2.2.2 assessment; 100% because continuously energized | 0.1414 kW | Cisco C1200-16P-2G; 17.2 W system power, 120 W PoE budget, 141.4 W worst-case with PoE. | REF-OF-09
Office (Communication) | LD-OF-10 | WAN/router | 1 | 230 V 1φ | 24.8 W max | Continuous | AS/NZS 3000 Cl.2.2.2 assessment; 100% | 0.0248 kW | Cisco ISR representative rating, PSU loss excluded from published figure. | REF-OF-10
Office (Communication) | LD-OF-11 | UPS | 1 | 230 V 1φ | 1500 VA / 1000 W output capacity | Continuous | Supplies downstream comms loads; capacity not treated as additional load | Not additive | APC SMT1500IC. UPS losses/recharge checked separately. | REF-OF-11
Office (Communication) | LD-OF-12 | UPS recharge check |  |  | Charger 136 W | Temporary operating condition | Downstream MD + charger | ≈0.302 kW + conversion losses | Not part of normal MD. | REF-OF-12
Office (Kitchenette) | LD-OF-13 | Kettle | 1 | 220–240 V, 1φ | 2.0–2.4 kW | Intermittent / automatic shut-off | heating/cooling/appliance group calculation AS/NZS 3000, table C2, Group (c) , colomn 3 | Calculated at Table C2 group (c) | Breville Crystal Luxe BKE765. Manufacturer specifies 2000–2400 W, 220–240 V and automatic shut-off. For design, use maximum published input 2.40 kW. | REF-OF-13
Office (Kitchenette) | LD-OF-14 | Microwave | 1 | 230–240 V, 1φ, 50 Hz | 1.33 kW electrical input | Intermittent | heating/cooling/appliance group calculation AS/NZS 3000, table C2, Group (c) , colomn 3 | Calculated at Table C2 group (c) | Panasonic NN-ST34NWQPQ. Manufacturer specifies 230–240 V / 50 Hz and 1330 W power consumption. Note that 900 W is microwave output, not electrical input. | REF-OF-14
Office (Kitchenette) | LD-OF-15 | Toaster | 1 | 220–240 V, 1φ, 50–60 Hz | 0.84–1.00 kW | Intermittent | heating/cooling/appliance group calculation AS/NZS 3000, table C2, Group (c) , colomn 3 | Calculated at Table C2 group (c) | Breville Toast Select Luxe BTA735. Manufacturer specifies 840–1000 W, 220–240 V. Design uses maximum published input 1.00 kW. | REF-OF-15
Office (Kitchenette) | LD-OF-16 | Commercial underbench refrigerator | 1 | 220–240 V, 1φ, 50 Hz | 138 L; 280 W electrical power; 1.2 A rated current | Cycling / automatic | heating/cooling/appliance group calculation AS/NZS 3000, table C2, Group (c) , colomn 3 | Calculated at Table C2 group (c) | Bromic UBC0140SD-NR commercial underbench fridge. Manufacturer gives 138 L, 220–240 V, 1.2 A; current user manual gives 280 W electrical power Suitable as a conceptual small-office commercial refrigerator, sizing is an engineering assumption | REF-OF-16
Office (Amenities) | LD-OF-17 | Storage hot-water unit | 1 | 230–240 V, 1φ | 50 L, 1.8 kW element | Cycling / thermostatic | AS/NZS 3000, table C2, group (g) Full load | 1.80 kW | Rheem 191050 representative 50 L electric storage HWS. 1.8 kW element selected for conceptual design; retain original Rheem manufacturer reference from Rev 0. | REF-OF-17
Workshop | LD-WS-01 | General-purpose socket outlets | 10 double GPO = 20 outlets | 230 V, 1φ, 10 A | 10 A per outlet | Mixed / intermittent | AS/NZS 3000 non-domestic socket-outlet calculation Table C2 Group (b)(i), Column 3: first outlet 1000 W + 750 W per additional outlet | 15.25 kW | Quantity derived from workshop function/layout: 3 double GPO per maintenance bay ×2, 2 at workbench, 1 battery/tool area, 1 general service point. Non-office outlet quantity based on intended use rather than floor-area rule, consistent with Curtin Electrical Services Guidelines. Double GPO counts as two socket-outlet points. Industrial/weather-resistant GPO type to be selected to suit environmental exposure; Clipsal 56 Series IP66 used as representative product reference. | REF-WS-01
Workshop | LD-WS-02 | Screw air compressor | 1 | 415 V 3φ | 11 kW mechanical output | Cycling / automatic; capable of 100% duty | AS/NZS 3000 Table C2 Group (d) Largest motor: 100% | Calculated at Table C2 group (d) | 1. Atlas Copco G11 retained; 11 kW installed motor, 100% duty capability. Final connected electrical load should use actual package FLC/PF/efficiency, not simply treat 11 kW shaft/motor rating as exact grid input. 2. No specific efficiency data, use ABB motors as reference. | REF-WS-02
Workshop | LD-WS-03 | Vehicle hoist | 1 | 415 V 3φ | 3 kW Mechanical output | Intermittent | AS/NZS 3000 Table C2 Group (d) Second-largest motor: preliminary 75% contribution | Calculated at Table C2 group (d) | From Molnar CM245-A retained: 4.5 t vehicle hoist, 3 kW motor output, 3-phase 50 Hz, 7 A. Molnar did not provide efficiency and PF data. Therefore, motor electrical input estimated from 3 kW mechanical output using η = 0.88 and PF = 0.80 lagging, based on representative 3 kW, 415 V industrial induction motor data. Manufacturer-listed 7 A kept as equipment supply-current reference. | REF-WS-03
Workshop | LD-WS-04 | Maintenance welding supply | 1 | 240 V 1φ | 240 V, 1φ; I effective =15 A; PF=0.99 | Intermittent | Maximum Demand = 3.60 kVA AS/NZS 3000 Appendix C, C2.5.2,C2.5.2.2 Arc welding machines, 100% rated primary current (I eff). | 3.60 kVA | Lincoln Powercraft 250M: 240 V / 15 A, general maintenance/fabrication application. | REF-WS-04
Workshop | LD-WS-05 | Welding fume extractor | 1 | 230 V 1φ | 1 kW | Intermittent; coincident with welding | Group (h) Engineering assessment according to AS/NZS 3000 Cl. 2.2.2 full connected load, because fume extraction is required coincidentally with welding operation. | 1.000 kW | New Rev 1 item. WorkSafe WA identifies LEV as an engineering control for welding fumes; Nederman FE840 is specifically suitable for maintenance welding and has 1 kW input. | REF-WS-05
Workshop | LD-WS-06 | LED high-bay lighting | 8 preliminary | 230/240 V | 120 W max/fitting; ~20,000 lm/fitting | Continuous when workshop occupied | 100% lighting load AS/NZS 3000 Table C2(a) column 3 | 0.960 kW | Revised from 6 → 8 due to 274.5 m² footprint. Australian utility specification references AS 1680.2.4 and uses 400 maintained lux for maintenance-workshop assembly/maintenance areas. Eight × 20,000 lm gives 160,000 source lumens versus 109,800 lm at 400 lx before utilisation/maintenance losses; therefore 8 is a reasonable preliminary quantity only. Final photometric model required. | REF-WS-06
Workshop | LD-WS-07 | Motorised roller doors | 2 | 415 V 3φ | 0.75 kW Mechanical output | Intermittent / low-cycle | AS/NZS 3000 Table C2 Group (d) both are remaining motors 50% each | Calculated at Table C2 group (d) | Grifco ML6103 E-Drive: 0.75 kW, 415 V 3φ, 2.3 A, low-cycle, max door 36 m². Qty 2 adopted as conceptual two-bay access arrangement, supported by comparable Australian 15×18 m workshop designs using two roller doors. Manufacturer Grifco specifies 0.75 kW motor rating and 2.3 A but does not provide efficiency or power factor. ≈1.65 kVA each; ≈3.31 kVA total Electrical input estimated assuming η=0.68, based on representative 0.75 kW, 415 V induction motor data, data from ABB | REF-WS-07
Workshop | LD-WS-08 | General dilution / roof exhaust ventilation | 0 mechanical fans in Rev 1 | — | — | Natural ventilation | No mechanical load currently installed, using natual ventilation | 0 kW | Base design adopts natural ventilation for the open/semi-open maintenance shelter, with dedicated welding LEV separately provided. Natural-ventilation compliance to be checked against AS 1668.4:2024. If enclosure/opening arrangement changes, reopen this item and design mechanical ventilation to AS 1668.2:2024. Safe Work Australia notes natural ventilation may be suitable for small workshops with one or two vehicles. | REF-WS-08
Workshop | LD-WS-09 | General tools / battery chargers / portable equipment | 3 representative items | 230 V 1φ | 470 W charger + 250 W bench grinder + 840 W angle grinder | Intermittent / user-controlled | AS/NZS 3000 non-domestic socket-outlet calculation Table C2 Group (b)(i), Column 3: first outlet 1000 W + 750 W per additional outlet | Included in GPO Group calculation Table C2 Group (b)(i), Column 3 | Milwaukee M18 dual-bay charger 470 W max input; Makita GB602 250 W bench grinder; Makita 9558HN 840 W angle grinder. Used to validate realistic workshop GPO usage rather than as an additional diversified load. | REF-WS-09
External | LD-EXT-01 | Building / perimeter floodlighting | 4 | 240 V 1φ | 100 W setting each | Continuous at night | AS/NZS 3000 Table C2 Group (a), Column 3 full connected lighting load | 0.400 kW | Existing four-corner conceptual arrangement retained. Pierlite MaxiMaster Gen3 supports selectable 100/150/200/250 W settings and is intended for industrial/commercial area lighting. Outdoor lighting layout to be verified against AS/NZS 1158.3.1:2020 + Amd 1:2024 where pedestrian/access-area lighting applies, and spill/obtrusive light against AS/NZS 4282:2023. | REF-EXT-01
All Building | LD-GEN-01 | Emergency / exit lighting | 3 maintained exit signs + 4 emergency luminaires | 240 V 1φ | Exit signs 4.6 W each; emergency luminaires 2.5 W each | Exit signs maintained continuously; emergency luminaires non-maintained / battery-backed | 100% concept connected load; treated conservatively as lighting load for MD. Emergency system design governed by NCC Part E4 and AS/NZS 2293.1:2026 | 0.024 kW | Concept basis: 1 office egress + 2 workshop egress locations, plus one additional emergency luminaire at the internal/transition path. Pierlite Director 2 exit sign = 4.6 W; Firefly 2 emergency luminaire = 2.5 W max. Final location/spacing to be verified against NCC 2022 Part E4, AS/NZS 2293.1:2026, and product compliance to AS/NZS 2293.3:2026. | REF-ALL-01
MSB | / | Future expansion spare feeder | 1 | 415 V 3φ | Capacity TBD after current MD calculation | Standby / unused | Not part of current maximum demand. Future capacity is handled separately as design spare / future scenario | 0 kW current | Spare outgoing feeder provided for future expansion. Do not invent a fictitious future load. After current facility MD is calculated, use a project design allowance; a 25% spare-capacity criterion is defensible as a conceptual owner-design benchmark because UWA's published electrical design standard specifies a general minimum 25% spare allowance for transformers, switchgear, feeders, MSBs and DBs. This is a project criterion, not an AS/NZS 3000 requirement. | REF-ALL-01
Note: Loads are grouped by physical location for equipment identification only. Load-group classification and maximum demand calculations are addressed separately.
Reference List
Reference ID | URL
REF-OF-01 | https://properties.curtin.edu.au/wp-content/uploads/sites/5/2021/02/electrical-services-guidelines-v4-aug.pdf
REF-OF-02 | https://www.dell.com/en-au/shop/dell-65w-usb-c-adapter/apd/450-bfxc/pc-accessories?msockid=0421427fe1226c8d0ea554d9e0d36d92
REF-OF-03 | https://www.brother.com.au/-/media/ap2/australia/products/common/brochures/mfc-l2880dw-xl---brochure.pdf?rev=a66a68b91af14ebd89b4b52721340515
REF-OF-04 | https://www.shreddersonline.com.au/home-office/181-fellowes-99ci-cross-shredder.html
REF-OF-05 | https://www.dimplex.com.au/sites/g/files/emiian331/files/2020-08/DimplexCooling_Specs-2020-21_DCACP30DC.pdf
REF-OF-06 | https://www.fantech.com.au/FanDataPrint.aspx?MountingID=WE&Pid=SILDES300CZ3C-S&Product=silent-design-series&RangeID=2027
REF-OF-07 | https://www.mhiaa.com.au/products/series/split-system-air-conditioners-bronte-series/
REF-OF-08 | https://pierlite.com.au/resources/Resource%20Assets/Pierlite%20Fast%20Movers%20February%202025_Medium%20Res.pdf
REF-OF-09 | https://www.cisco.com/c/en/us/products/collateral/switches/catalyst-1200-series-switches/nb-06-cat1200-ser-data-sheet-cte-en.html
REF-OF-10 | https://www.cisco.com/c/en/us/products/collateral/routers/1000-series-integrated-services-routers-isr/datasheet-c78-739512.html
REF-OF-11 | https://www.se.com/au/en/product/SMT1500IC/apc-smartups-line-interactive-1500va-tower-230v-8x-iec-c13-outlets-smartconnect-port%2Bsmartslot-avr-lcd/
REF-OF-12 | https://www.ijk.com.au/branch/ijk/product/162487p280_711/SMT1500IC.html
REF-OF-13 | https://www.breville.com/au/en/product/bke765?sku=BKE765BSS4JAN1
REF-OF-14 | https://www.panasonic.com/au/consumer/household/microwave-ovens/microwave-only/nn-st34nwqpq.specs.html
REF-OF-15 | https://www.breville.com/en-au/product/bta735?sku=BTA735SSB2IAN1
REF-OF-16 | https://portalimages.blob.core.windows.net/products/pdfs/5fkmyx5w_UBC0140SD-NR_SPEC_0525.pdf
REF-OF-17 | https://www.rheem.com.au/rheem/products/Residential/Electric/Rheem-111-191-Series-Electric/Rheem-50L-Electric-Water-Heater/p/191050G4
REF-WS-01 | https://properties.curtin.edu.au/wp-content/uploads/sites/5/2021/02/electrical-services-guidelines-v4-aug.pdf https://www.se.com/au/en/product/56C310D-GY/switched-socket-outlet-clipsal-56-series-250v-10a-3-flat-pin-ip66-2-pole/
REF-WS-02 | https://www.atlascopco.com/en-au/compressors/air-compressor/2-18kw-screw-compressor/11-kw-screw-air-compressor https://library.e.abb.com/public/391ef7da01144b5382c13d0bbe3bf5a7/11KW%204P%20IE2.pdf?x-sign=1bVTuqcjEMJz0V6D3gRy30EgeDuRJ%2B0OWV8xlHScy7b2RVDX5qKrfFALfrocdG4u
REF-WS-03 | https://molnarhoists.com.au/product/cm245-a-2-post-symmetrical-car-hoist-4-5tonne/ https://witmermotor.com/products/00318et3wal100lff-w22-weg-4hp-3kw-iec-tru-metric-electric-motor-1800rpm?variant=43915733270621
REF-WS-04 | https://ch-delivery.lincolnelectric.com/api/public/content/55d9de03fb674f248c2313e9a9df607f?v=2acb76f5
REF-WS-05 | https://www.worksafe.wa.gov.au/local-exhaust-ventilation
REF-WS-06 | https://www.urbanutilities.com.au/sfsites/c/cms/delivery/media/MCS2XRTMIP25DOVBL5VMJWJL4KD4
REF-WS-07 | https://www.grifco.com.au/product/e-drive/ https://library.e.abb.com/public/108586d435f94a29965936dca57eaa16/0.75kw%204p.pdf?x-sign=l5lqmqRGKb9aCrxKkCd+Zdzmwvxm5EfCVWsfyEoX5F8i6I5IIKUG4gk2OBsCwxOW
REF-WS-08 | https://www.buildinginformationgateway.com.au/library/as-1668.4-2024-the-use-of-ventilation-and-airconditioning-in-buildings-part-4-natural-ventilation-of-buildings
REF-WS-09 | https://www.milwaukeetool.com.au/on/demandware.static/-/Sites/en_AU/v1749844943985/ProductResources/Powertools/Battery%20%26%20Chargers/M18DBSC-User-Manual.pdf
REF-EXT-01 | https://pierlite.com.au/resources/Resource%20Assets/Pierlite%20Fast%20Movers%20February%202025_Medium%20Res.pdf
REF-ALL-01 | https://pierlite.com.au/resources/Resource%20Assets/Pierlite%20Fast%20Movers%20FY%202024-2025%20%28MED%20RES%29.pdf
REF-ALL-01 | https://www.uwa.edu.au/about/-/media/project/uwa/uwa/about/docs/campus-management/facilities-management/c-uwa-design-and-construction-standards-electrical-services-2-2.pdf

## Load Flow Input Analysis
Feeder | AS/NZS 3000 Classification (Load Group in Table C2) | Load Description | Phase Basis | P (kW) | Q (kVAr) | S (kVA) | PF | Calculation Details | Notes | Ref Number
Office | (a) Lighting other than Group (f) also devices permanently installed and <150w | Office LED lighting+ toilet exhaust fan. | 1φ loads, later balanced across 3φ | 0.308 | 0.145 | 0.34 | 0.905 lagging | For LED: Q = P·tan(cos⁻¹0.90)=0.288·tan(cos⁻¹0.90)=0.139 For fan: S=0.0207 kVA PF=0.020/0.0207≈0.966 Q=S·sin(cos⁻¹PF)=0.0207·sin(cos⁻¹0.966)=0.005351 P subtotal=0.308, Q subtotal=0.145, S subtotal =0.34, 0.905 lagging. | 1. Pierlite eco panel gen3 datasheet gives PF >0.9, use 0.90 conservatively for the LED panels. 2. Fantech fan gives 20 W and 0.09 A at 230 V, Add P and Q vectorially for the group. | REF-OF-01
| (b)(ii) Socket-outlets ≤10 A with permanently installed HVAC | Office general GPO aggregate | 1φ mixed loads, later balanced across 3φ | 3.9 | 1.889 | 4.333 | 0.90 lagging | S = P/PF=3.9/0.9=4.333 Q = √(S²-P²)=1.889 | No single manufacturer PF exists because this is an aggregate of laptops, monitor, printer, shredder, fan and miscellaneous office equipment. Use PF=0.90 lagging as a conservative aggregate assumption at this stage, not an AS/NZS 3000 value. ABB notes modern computer/SMPS office loads can be around PF 0.9, while Schneider shows motor PF can be lower and resistive loads ≈1; 0.90 avoids assuming beneficial reactive cancellation. https://library.e.abb.com/public/ba2689ca7969413a8e10f38101d5e337/9AKK107992A9345_Building Solutions_OFFICE_ebook_v3_small.pdf?x-sign=0FMZNAj2sfBW%2FdNZeJ7ZXfkONQtH7vvu2ZU7bNFXuyEuT505HUEgRl451gMcNUtc | REF-OF-02
| (c)(i) Cooking, heating and cooling appliances | HVAC ×2 + kettle + microwave + toaster + refrigerator | Predominantly 1φ, later balanced across 3φ | 10.145 | 3.236 | 10.65 | 0.953 lagging | HVAC: MHI gives max input 3.65 kW, 240 V and max current 17 A → S=4.08 kVA, PF=0.895, Q=1.82kVar Fridge: 280 W, 240 V, 1.2 A → S=0.288 kVA, PF=0.972,Q=0.068kVar Kettle and toaster treated as resistive, PF=1. Therefore, P=3.4kW, Q=0kVar Microwave also assumed resistive: P=1.330kW, PF=1, S=1.330kVA, Q=0kVar P subtotal = 3.65+0.75(3.65+0.280+3.400+1.330)=10.145 kW Q subtotal = 1.82+0.75(1.82+0.068)=3.236 kVAr S subtotal = √(P²+Q²)=10.65kVA | Calculated component-by-component. Apply AS/NZS 3000 MD factors to both P and Q: largest appliance 100%, remainder 75%. HVAC: MHI gives max input 3.65 kW, 240 V and max current 17 A → S=4.08S=4.08 kVA, PF≈0.895PF≈0.895. Fridge: 280 W, 240 V, 1.2 A → S=0.288S=0.288 kVA, PF≈0.972PF≈0.972. Kettle/toaster treated as resistive, PF≈1. Microwave manufacturer gives 1300–1400 W and 5.4–6.1 A over 230–240 V, therfore assuming approximately unity PF at rated condition. | REF-OF-03
| (g) Thermal-storage heating elements | Storage hot-water system | 1φ | 1.8 | 0 | 1.8 | 1 | P=1.8kW, PF=1, Q=0, S01.8kVA | Resistive heating element. For concept load flow use PF≈1 and therefore Q≈0. Schneider typical PF data gives resistance heating equipment at unity PF. (Electrical Installation) https://www.electrical-installation.org/enwiki/Practical_values_of_power_factor | REF-OF-04
| (j) Other equipment not covered above — by assessment | Communications: PoE switch + WAN/router via UPS | 1φ | 0.166 | 0.08 | 0.185 | 0.90 lagging | P=0.166kW, PF=0.9, S=P/P​F=0.166​/0.9=0.185 kVA, Q=√(S²-P²)=√(0.184²−0.166²)=0.080 kVAr | Cisco datasheets do not provide a usable aggregate input PF for this combination. Use PF=0.90 lagging as a conservative concept-stage IT-load assumption. ABB notes modern computer/electronic office loads can be around PF 0.9; using lagging rather than assuming capacitive cancellation is conservative for transformer sizing. UPS output capacity is not additive; battery recharge is excluded from LF-01 normal operation. https://library.e.abb.com/public/ba2689ca7969413a8e10f38101d5e337/9AKK107992A9345_Building Solutions_OFFICE_ebook_v3_small.pdf?x-sign=0FMZNAj2sfBW%2FdNZeJ7ZXfkONQtH7vvu2ZU7bNFXuyEuT505HUEgRl451gMcNUtc | REF-OF-05
Office Subtotal |  |  |  | 16.319 | 5.35 | 17.1736 | 0.95 lagging | P=ΣPi; Q=ΣQi; S=√(P²+Q²); PF=P/S
Workshop | (a) Lighting other than Group (f) | Workshop high-bay lighting | 1φ loads, later balanced across 3φ | 0.96 | 0.465 | 1.067 | 0.90 lagging | P=0.96 kW, PF=0.90, S=P/PF=0.96/0.90=1.067 kVA, Q=√(S²−P²)=√(1.067²−0.96²)=0.465 kVAr | Exact Pierlite PF is not stated in the published product data we have. Schneider gives LED lighting PF >0.9; for concept design use the conservative lower-bound PF = 0.90. https://www.electrical-installation.org/enwiki/Calculation_of_voltage_drop_in_steady_load_conditions | REF-WS-01
| (b)(i) Socket-outlets ≤10 A | Workshop general-purpose outlets / portable tools aggregate | 1φ loads, later balanced across 3φ | 15.25 | 11.438 | 19.063 | 0.80 lagging | P=15.25 kW, PF=0.80, S=P/PF=15.25/0.80=19.063 kVA, Q=√(S²−P²)=√(19.063²−15.25²)=11.438 kVAr | No single PF exists for this mixed outlet load. Concept-stage PF = 0.80 lagging is adopted conservatively because the representative mix is tool/motor-heavy plus electronic chargers. Schneider gives ordinary induction-motor PF around 0.80 at 75% load and 0.85 at full load. This is an engineering assumption, not an AS/NZS 3000 prescribed PF. (Electrical Installation) https://www.electrical-installation.org/enwiki/Practical_values_of_power_factor | REF-WS-02
| (d) Motors other than Groups (e) and (f) | Compressor 100% + vehicle hoist 75% + roller-door motors 50% each | 3φ | 15.91 | 12.875 | 20.467 | 0.777 lagging | I. Compressor(Largest): S = √3VI; P = S·PF; Q = √(S²-P²) Pin=11/0.898=12.25 kW, PF=0.81, S=P/PF=12.25/0.81=15.123 kVA, Q=√(S²−P²)=√(15.123²−12.25²)=8.869 kVAr. Full load. II. Hoist(Second largest): Pin=3/0.88=3.409 kW, S=√3VI=√3×415×7/1000=5.032kVA, Q=√(S²−P²)=√(5.032²−3.409²)=3.70 kVAr, PF=P/S=3.409/5.032=0.677 75% Load III. Roller doors(Remainder): Pin=0.75/0.68=1.103 kW, S=√3VI=1.653kVA, Q=√(S²−P²)=√(1.653²−1.103²)=1.231 kVAr, PF=0.667 2 roller doors with 50% load each. | Highest: full load; Second highest: 75% load; remainder: 50% full load.Calculated motor-by-motor; I. Compressor: 1. Atlas Copco G11 retained; 11 kW installed motor, 100% duty capability. Final connected electrical load should use actual package FLC/PF/efficiency, not simply treat 11 kW shaft/motor rating as exact grid input. 2. No specific efficiency data, use ABB motors as reference. From ABB Motor 11 kW、415 V、50 Hz、4-pole: (rated current = 21 A, PF = 0.81, efficiency = 89.8%). II. Hoist: From Molnar CM245-A retained: 4.5 t vehicle hoist, 3 kW motor output, 3-phase 50 Hz, 7 A. Molnar did not provide efficiency and PF data. Therefore, motor electrical input estimated from 3 kW mechanical output using η = 0.88, based on representative 3 kW, 415 V industrial induction motor data. Estimation data from Witmer Manufacturer-listed 7 A kept as equipment supply-current reference III. Roller Doors: Grifco ML6103 E-Drive: motor rating 0.75 kW, 415 V 3φ, 2.3 A, but does not provide efficiency or power factor. Therefore electrical input conservatively estimated assuming η=0.667, based on representative 0.75 kW, 415 V induction motor data, data from ABB. | REF-WS-03
| (h) Welding machines | Maintenance welder | 1φ | 3.564 | 0.508 | 3.6 | 0.99 lagging | S=240×15=3.6S=24015=3.6 kVA P=S*PF=3.6×0.99=3.564 Q=√(S²−P²)=√(3.600²−3.564²)=0.508 kVAr | Lincoln Powercraft 250M gives Ieff = 15 A, 240 V and PF = 0.99. AS/NZS 3000 MD uses the rated primary/effective current. https://powercraft-lincolnelectric.com.au/wp-content/uploads/2023/05/IM7908-14-Powercraft-250M-Operator-Manual.pdf | REF-WS-04
| (j) Other equipment — by assessment | Welding fume extractor, 100% coincident with welding | 1φ | 1 | 0.75 | 1.25 | 0.80 lagging | P=1.000 kW, PF=0.80, S=P/PF=1.000/0.80=1.250 kVA, Q=√(S²−P²)=√(1.250²−1.000²)=0.750 kVAr | Nederman FE840 documentation identifies a 230/240 V, 1 kW motor, but does not publish a usable PF. Use PF = 0.80 lagging as conservative assumption; replace with actual input current/PF if obtained. https://www.nederman.com/catalog-images/resources/423438/original/user manual - fe840-fe841_423438.pdf | REF-WS-05
Workshop Subtotal |  |  |  | 36.684 | 26.036 | 44.9843 | 0.815 lagging | P=ΣPi; Q=ΣQi; S=√(P²+Q²)
External | (a) Lighting other than Group (f) | External floodlighting + emergency / exit lighting | 1φ loads, later balanced across 3φ | 0.424 | 0.205 | 0.471 | 0.90 lagging | P=0.424 kW, PF=0.90,S=P/PF=0.424/0.90=0.471 kVA, Q=√(S²−P²)=√(0.471²−0.424²)=0.205 kVAr | LED-driver load. Published MaxiMaster data confirm the 100 W LED floodlight but no PF provided; use generic LED PF >0.9, conservatively set to 0.90. Emergency/exit load is only 24 W, so using the same equivalent PF is immaterial at this stage. https://shop.cnw.com.au/medias/Pierlite-MaxiMaster-Floodlight-Gen3-Datasheet.pdf?context=bWFzdGVyfHJvb3R8NDQwMDAxMHxhcHBsaWNhdGlvbi9wZGZ8YURCaEwyaGtPUzh4TURnMU16WXpNVE01TXpneU1pOVFhV1Z5YkdsMFpTQk5ZWGhwVFdGemRHVnlJRVpzYjI5a2JHbG5hSFFnUjJWdU15QXRJRVJoZEdGemFHVmxkQzV3WkdZfDAwOGViYTRmOWY3Mjc2N2QwODY2OTVjODk2ZjUzNjMzZTEyZDhhYTkxNzNmNDhkOGQ3NmM3ZjhlY2FiODM0ZGQ | REF-EXT-01
External Subtotal |  |  |  | 0.424 | 0.205 | 0.471 | 0.90 lagging
Total |  |  |  | 53.427 | 31.591 | 62.068 | 0.861 lagging
Notes: 1. This table provides the detailed maximum-demand analysis and derives the P, Q, S and PF values required for power factory load-flow modelling. 2. P, Q, S and PF represent the Rev 01 maximum-demand values adopted for load-flow analysis. They do not represent raw connected loads or equipment nameplate ratings. Positive Q denotes lagging reactive-power demand. 3. The External Feeder is temporarily incorporated into the Office Feeder calculation. A dedicated External Feeder will be assessed once the final external loads are confirmed.
Ref Number | Notes
REF-OF-01 | https://pierlite.com.au/resources/Resource%20Assets/Pierlite%20Fast%20Movers%20February%202025_Medium%20Res.pdf
REF-OF-02 | https://library.e.abb.com/public/ba2689ca7969413a8e10f38101d5e337/9AKK107992A9345_Building Solutions_OFFICE_ebook_v3_small.pdf?x-sign=0FMZNAj2sfBW%2FdNZeJ7ZXfkONQtH7vvu2ZU7bNFXuyEuT505HUEgRl451gMcNUtc
REF-OF-03 | https://www.mhiaa.com.au/products/series/split-system-air-conditioners-bronte-series/
REF-OF-04 | https://www.electrical-installation.org/enwiki/Practical_values_of_power_factor
REF-OF-05 | https://library.e.abb.com/public/ba2689ca7969413a8e10f38101d5e337/9AKK107992A9345_Building Solutions_OFFICE_ebook_v3_small.pdf?x-sign=0FMZNAj2sfBW%2FdNZeJ7ZXfkONQtH7vvu2ZU7bNFXuyEuT505HUEgRl451gMcNUtc
REF-WS-01 | https://www.electrical-installation.org/enwiki/Calculation_of_voltage_drop_in_steady_load_conditions
REF-WS-02 | https://www.electrical-installation.org/enwiki/Practical_values_of_power_factor
REF-WS-03 | https://www.mhiaa.com.au/products/series/split-system-air-conditioners-bronte-series/
REF-WS-04 | https://powercraft-lincolnelectric.com.au/wp-content/uploads/2023/05/IM7908-14-Powercraft-250M-Operator-Manual.pdf
REF-WS-05 | https://www.nederman.com/catalog-images/resources/423438/original/user manual - fe840-fe841_423438.pdf
REF-EXT-01 | https://shop.cnw.com.au/medias/Pierlite-MaxiMaster-Floodlight-Gen3-Datasheet.pdf?context=bWFzdGVyfHJvb3R8NDQwMDAxMHxhcHBsaWNhdGlvbi9wZGZ8YURCaEwyaGtPUzh4TURnMU16WXpNVE01TXpneU1pOVFhV1Z5YkdsMFpTQk5ZWGhwVFdGemRHVnlJRVpzYjI5a2JHbG5hSFFnUjJWdU15QXRJRVJoZEdGemFHVmxkQzV3WkdZfDAwOGViYTRmOWY3Mjc2N2QwODY2OTVjODk2ZjUzNjMzZTEyZDhhYTkxNzNmNDhkOGQ3NmM3ZjhlY2FiODM0ZGQ