## Sheet1
Topic | Design Basis / Decision | Reference / Source
Project Scope | Conceptual electrical distribution design for a small WA mining office and workshop. Current scope contains preliminary SLD, maximum demand, cable sizing, load flow, short circuit and preliminary protection studies. | Project definition
System Voltage Hierarchy | Using 33 kV → 11 kV → 415 V distribution architecture. | Future Power WA, Granny Smith Mining https://futurepowerwa.com.au/project/granny-smith-mining/
33/11 kV Substation | Retain an upstream 33/11 kV substation so the 11 kV system can supply green valley and allow future expansion. | Future Power WA, Granny Smith Mining https://futurepowerwa.com.au/project/granny-smith-mining/
11 kV Distribution | Supply green valley from the 11 kV bus through a dedicated 11 kV feeder. | Future Power WA mining-project references
RMU Arrangement | Provide an 11 kV RMU upstream of the green valley distribution transformer. | Future Power WA, Mt Morgans Gold Mine Upgrade https://futurepowerwa.com.au/project/mt-morgans-gold-mine-upgrade/ Future Power WA, Nova Nickel Mine https://futurepowerwa.com.au/project/nova-nickel-mine/
Kiosk / Transformer Arrangement | Use an RMU-fed 11/0.415 kV transformer arrangement, with transformer and LV distribution equipment located in the same electrical area. | Future Power WA, Mt Morgans Gold Mine Upgrade https://futurepowerwa.com.au/project/mt-morgans-gold-mine-upgrade/
LV System Voltage | Use 415/230 V three-phase four-wire LV distribution. | Western Power Network Voltage https://www.westernpower.com.au/resources-education/consumer-advice/understanding-your-power/our-network-voltage/
LV Distribution | 415 V MSB supplies separate Office DB and Workshop DB feeders, with spare ways retained for future expansion. | Green Valley design development
Office Basis | Preliminary 72 m² office with 8 staff, lighting, HVAC, GPO loads, communications, kitchenette and amenities. | Equipment/manufacturer references and project load schedule https://ausco.com.au/buildings/project-office-12m-x-6m
Workshop Basis | Preliminary 15 m × 18.3 m maintenance workshop with compressor, hoist, welding, LEV, lighting, roller doors and general-purpose outlets. | Gold Fields St Ives–Invincible scale reference https://www.domeshelter.com.au/case-study/gold-fields/ ; equipment manufacturer data
Maximum Demand Method | Determine maximum demand using AS/NZS 3000 Appendix C / Table C2 load classifications and engineering assessment where required. | AS/NZS 3000 – Electrical installations (wiring rules)
Spare Capacity Criterion | Apply a 25% project spare-capacity allowance for preliminary sizing and future expansion. | UWA electrical services design standard
Distribution Transformer | Preliminary selection: 100 kVA, 11/0.415 kV, Dyn11. Final selection subject to motor starting, voltage drop and fault studies. | Rev 01 maximum demand + 25% spare capacity check